## Sheet1
Mapping Points | Modbus Address | Data type
ActiveCoolHeatSetpointTemp | 40003 | Float
ActiveCurrentLimitSetpoint | 40007 | Float
EvapRefrigerantPressure-Ckt1 | 40011 | Float
EvapRefrigerantPressure-Ckt2 | 40013 | Float
CondenserRefrigerantPressure-Ckt1 | 40019 | Float
CondenserRefrigerantPressure-Ckt2 | 40023 | Float
RunTime-Comp2B | 40025 | Float
Starts-Comp1A | 40029 | Float |  |  | Modbus ID
Starts-Comp1B | 40031 | Float |  | Chiller1 | 1
Starts-Comp2A | 40033 | Float |  | Chiller2 | 2
Starts-Comp2B | 40035 | Float |  | Chiller3 | 3
RunTime-Comp1A | 40037 | Float
RunTime-Comp1B | 40039 | Float
RunTime-Comp2A | 40043 | Float |  | Port | Baud | Parity | Data_Bits | Stop_Bits
Line2Current(inAmps)-Comp2A | 40047 | Float |  | R1 | 9600 | None | 8 | 1
EvapLeavingWaterTemp | 40049 | Float
HighSideOilPressure-Comp1A | 40051 | Float
HighSideOilPressure-Comp1B | 40053 | Float
HighSideOilPressure-Comp2A | 40055 | Float
HighSideOilPressure-Comp2B | 40057 | Float
OilTemp-Comp1A | 40059 | Float
OilTemp-Comp1B | 40061 | Float
OilTemp-Comp2A | 40063 | Float
EvapEnteringWaterTemp | 40065 | Float
OilTemp-Comp2B | 40067 | Float
PhaseABVoltage-Comp1A | 40069 | Float
Line1Current(inAmps)-Comp1A | 40071 | Float
Line2Current(inAmps)-Comp1A | 40073 | Float
Line3Current(inAmps)-Comp1A | 40075 | Float
Line1Current(inAmps)-Comp1B | 40077 | Float
Line2Current(inAmps)-Comp1B | 40079 | Float
Line3Current(inAmps)-Comp1B | 40081 | Float
Line1Current(inAmps)-Comp2A | 40083 | Float
OutdoorAirTemp | 40085 | Float
Line3Current(inAmps)-Comp2A | 40087 | Float
Line1Current(inAmps)-Comp2B | 40089 | Float
Line2Current(inAmps)-Comp2B | 40091 | Float
Line1Current(%RLA)-Comp1A | 40093 | Float
Line2Current(%RLA)-Comp1A | 40095 | Float
Line3Current(%RLA)-Comp1A | 40097 | Float
Line1Current(%RLA)-Comp1B | 40099 | Float
Line2Current(%RLA)-Comp1B | 40101 | Float
Line3Current(%RLA)-Comp1B | 40103 | Float
Line1Current(%RLA)-Comp2A | 40105 | Float
Line2Current(%RLA)-Comp2A | 40107 | Float
Line3Current(%RLA)-Comp2A | 40109 | Float
Line1Current(%RLA)-Comp2B | 40111 | Float
Line2Current(%RLA)-Comp2B | 40113 | Float
Line3Current(%RLA)-Comp2B | 40115 | Float
ChilledWaterSetpoint | 40125 | Float | W
Line3Current(inAmps)-Comp2B | 40129 | Float
RunEnabled | 1 | bit
LocalSetpointControl | 2 | bit
ChillerRunningState | 3 | bit
Comp1ARunning | 6 | bit
Comp1BRunning | 7 | bit
Comp2ARunning | 8 | bit
Comp2BRunning | 9 | bit
ChillerAutoStopCommand | 15 | bit | W

## Sheet1 (2)
Mapping Points | Modbus Address | Data type |  |  | READ ADDRESS | SIZE | s.no | parameter | div | address | id | funtion type
ActiveCoolHeatSetpointTemp | 40003 | Float |  | 0 | FC4_0
ActiveCurrentLimitSetpoint | 40007 | Float |  | 1 | 2 |  | 1 | LCW SETPOINT | 1 | FC3_0 | (1,2,3) | HOLD REG
EvapRefrigerantPressure-Ckt1 | 40011 | Float |  | 2 | 4 |  | 2 | CHILLER START/STOP | 1 | FC3_1 | (1,2,3) | HOLD REG
EvapRefrigerantPressure-Ckt2 | 40013 | Float |  | 3 | 6
CondenserRefrigerantPressure-Ckt1 | 40019 | Float |  | 4 | 8
CondenserRefrigerantPressure-Ckt2 | 40023 | Float |  | 5 | 10
RunTime-Comp2B | 40025 | Float |  | 6 | 12
Starts-Comp1A | 40029 | Float |  | 7 | 14 |  |  | Modbus ID
Starts-Comp1B | 40031 | Float |  | 8 | 16 |  | Chiller1 | 1
Starts-Comp2A | 40033 | Float |  | 9 | 18 |  | Chiller2 | 2
Starts-Comp2B | 40035 | Float |  | 10 | 20 |  | Chiller3 | 3
RunTime-Comp1A | 40037 | Float |  | 11 | 22
RunTime-Comp1B | 40039 | Float |  | 12 | 24
RunTime-Comp2A | 40043 | Float |  | 13 | 26 |  | Port | Baud | Parity | Data_Bits | Stop_Bits
Line2Current(inAmps)-Comp2A | 40047 | Float |  | 14 | 28 |  | R1 | 9600 | None | 8 | 1
EvapLeavingWaterTemp | 40049 | Float |  | 15 | 30
HighSideOilPressure-Comp1A | 40051 | Float |  | 16 | 32
HighSideOilPressure-Comp1B | 40053 | Float |  | 17 | 34
HighSideOilPressure-Comp2A | 40055 | Float |  | 18 | 36
HighSideOilPressure-Comp2B | 40057 | Float |  | 19 | 38
OilTemp-Comp1A | 40059 | Float |  | 20 | 40
OilTemp-Comp1B | 40061 | Float |  | 21 | 42
OilTemp-Comp2A | 40063 | Float |  | 22 | 44
EvapEnteringWaterTemp | 40065 | Float |  | 23 | 46
OilTemp-Comp2B | 40067 | Float |  | 24 | 48
PhaseABVoltage-Comp1A | 40069 | Float |  | 25 | 50
Line1Current(inAmps)-Comp1A | 40071 | Float |  | 26 | 52
Line2Current(inAmps)-Comp1A | 40073 | Float |  | 27 | 54
Line3Current(inAmps)-Comp1A | 40075 | Float |  | 28 | 56
Line1Current(inAmps)-Comp1B | 40077 | Float |  | 29 | 58
Line2Current(inAmps)-Comp1B | 40079 | Float |  | 30 | 60
Line3Current(inAmps)-Comp1B | 40081 | Float |  | 31 | 62
Line1Current(inAmps)-Comp2A | 40083 | Float |  | 32 | 64
OutdoorAirTemp | 40085 | Float |  | 33 | 66
Line3Current(inAmps)-Comp2A | 40087 | Float |  | 34 | 68
Line1Current(inAmps)-Comp2B | 40089 | Float |  | 35 | 70
Line2Current(inAmps)-Comp2B | 40091 | Float |  | 36 | 72
Line1Current(%RLA)-Comp1A | 40093 | Float |  | 37 | 74
Line2Current(%RLA)-Comp1A | 40095 | Float |  | 38 | 76
Line3Current(%RLA)-Comp1A | 40097 | Float |  | 39 | 78
Line1Current(%RLA)-Comp1B | 40099 | Float |  | 40 | 80
Line2Current(%RLA)-Comp1B | 40101 | Float |  | 41 | 82
Line3Current(%RLA)-Comp1B | 40103 | Float |  | 42 | 84
Line1Current(%RLA)-Comp2A | 40105 | Float |  | 43 | 86
Line2Current(%RLA)-Comp2A | 40107 | Float |  | 44 | 88
Line3Current(%RLA)-Comp2A | 40109 | Float |  | 45 | 90
Line1Current(%RLA)-Comp2B | 40111 | Float |  | 46 | 92
Line2Current(%RLA)-Comp2B | 40113 | Float |  | 47 | 94
Line3Current(%RLA)-Comp2B | 40115 | Float |  | 48 | 96
ChilledWaterSetpoint | 40125 | Float | W | 49 | 98
Line3Current(inAmps)-Comp2B | 40129 | Float |  | 50 | 100
RunEnabled | 1 | bit |  | 51 | 102 | 1
LocalSetpointControl | 2 | bit |  | 52 | 103 | 1
ChillerRunningState | 3 | bit |  | 53 | 104 | 1
Comp1ARunning | 6 | bit |  | 54 | 105 | 1
Comp1BRunning | 7 | bit |  | 55 | 106 | 1
Comp2ARunning | 8 | bit |  | 56 | 107 | 1
Comp2BRunning | 9 | bit |  | 57 | 108 | 1
ChillerAutoStopCommand | 15 | bit | W | 58 | 109 | 1